Specification for an enclosed high pressure compressor and purification system to supply breathing air that meets or exceeds the requirements of CGA Pamphlet G-7, Compressed Air for Human Respiration, the requirements of ANSI/CGA G-7.1, Commodity Specification for Air, Grade E, and all other recognized standards for respirable air.  The compressor and purification system shall be manufactured by the same supplier.  The system shall be designed for a maximum working pressure of 5,000 PSIG.  All equipment shall be new and of current design and manufacture.  Used or refurbished equipment is unacceptable.  Specifications are subject to change without notice.

BAUER MODEL

## MVT20-E3

## MAXI-VERTICUS

# 5000 PSI SERVICE

The system shall be designed for “Against-The Wall” installation. The system shall be supplied on a vertical steel frame designed for both the static and dynamic loads of the system and of sufficient size to adequately accommodate all of the system’s components.

The system shall be supplied in a foam insulated cabinet enclosure for sound attenuation.  The enclosure shall incorporate a combination of lift-off and vertically hinged panels to permit access to the internal components for inspection and maintenance.  The design of the enclosure shall permit unrestricted cooling air flow to the compressor and prime mover, and provide access for operation, inspection and maintenance.

The system shall be designed for continuous duty operation indoors with room temperatures ranging between 40°F and 115°F.  Installation shall not require a special foundation; however, it is the responsibility of the purchaser to ensure the installation site has a solid and level foundation that can support the weight of the system, the availability of a qualified source of air for the intake of the compressor and adequate ventilation.

All piping and tubing shall be properly supported and protected to prevent damage from vibration during shipment, operation, or maintenance.  Piping and tubing shall be installed in a neat and orderly arrangement, adapting to the contours of the system.  All instrument tubing shall be 300 series stainless steel.

The system shall be warranted free from defects in material and workmanship for a period of eighteen months from date of shipment or twelve months from date of start-up, whichever expires first.  The warranty shall not impose limitations on the system’s accumulated operating hours during the warranty period.

Performance Table

| Model | FAD SCFM | Charging Rate SCFM | HP | RPM | Compressor Model | Purification System | Air Processing Capability (cu ft) |
| --- | --- | --- | --- | --- | --- | --- | --- |
| MVT 20 | 17.5 | 21.0 | 15.0 | 1300 | K150 II | P5 Securus | 150,000 |

Compressor

The compressor shall be an air-cooled, oil lubricated, four stage, four cylinder, single acting, reciprocating compressor.  The crankcase shall be cast of a high strength, aluminum alloy.  The crankshaft shall be of a single piece forged steel construction and supported in the crankcase by three long-life roller bearings.  The connecting rods shall be of single piece design and constructed of a high strength aluminum alloy.  Each connecting rod shall incorporate a roller bearing at the crank end and a needle bearing at the pin end.  The pistons shall be constructed of an aluminum alloy.  Piston rings on the first through third stage are of cast iron; fourth stage rings shall be of a high strength polymide.  The final stage shall incorporate a ringed, free-floating, aluminum piston, which is driven by a guide piston and third stage discharge pressure.  The cylinders shall be of cast iron construction with deep cooling fins on the external surface for optimum heat dissipation.  The cylinders shall be arranged in a dynamically balanced, diametrically opposed “X” configuration with each cylinder located directly in the cooling fan’s blast.  The cylinders shall be removable from the crankcase.  The compressor’s flywheel shall be cast iron.  A multi-wing, high velocity cooling fan shall be integral to the flywheel.  The fan wings shall be replaceable.

An intercooler shall be provided after each stage of compression and an aftercooler shall be provided after the final stage of compression.  The coolers shall be individually detachable from the compressor, located directly in the cooling fan’s blast and made of a stainless steel.  The aftercooler shall be designed to cool the discharge air to within 18°F of ambient temperature.  A cool-down cycle shall not be required prior to stopping the compressor.

A separator shall be supplied after each stage of compression, excluding the first stage, and a coalescing separator shall be supplied at the discharge of the compressor.  An automatic condensate drain (A.C.D.) system shall be supplied for all of the separators.  Adjustable drain timers shall be factory preset to drain the separators approximately every fifteen minutes for approximately six seconds.  The A.C.D. system shall unload the compressor on shutdown for unloaded restart.  An exhaust muffler and condensate reservoir shall be supplied.  Manually operated valves shall be supplied to override the automatic operation of the A.C.D. system for test and maintenance purposes.

The compressor shall be lubricated by a combination splash and low pressure lubrication system.  The final stage of compression shall be lubricated by a pressurized lubrication circuit.  The other stages and the driving gear shall be splash lubricated.  The pressure lubrication circuit shall include a positive displacement oil pump, gear driven by the crankshaft, and a non-adjustable oil pressure regulator.  A highly visible sight glass shall be included to check the oil level.  The oil drain for the compressor shall be piped to the outside of the frame.

Inter-stage pressures shall be monitored via locally mounted pressure gauges.

The compressor shall be equipped with an inlet filter with replaceable particulate elements.   An inlet filter maintenance indicator shall be included as part of the standard scope of supply and shall be integral to the inlet filter housing.

Prime Mover and V-Belt Drive

The electric motor shall be of the open drip-proof (ODP) design.  The motor voltage, phase and frequency shall be specified by the purchaser.  The compressor and motor shall be mounted on a common base that is vibration isolated from the system’s main frame.  The compressor and motor shall be arranged in a vertical design.  Power from the motor shall be transmitted to the compressor by a v-belt drive.  The v-belt drive shall be designed to tighten the drive belts automatically.  Rotation arrows shall be affixed in a conspicuous place on the compressor.

Electrical Control & Instrumentation

The compressor control panel (CCP) shall include an across-the-line magnetic motor starter, fused transformer and PLC controller. The CCP shall be built in accordance with UL 508A, the standard for Industrial Control Panels and shall be affixed with a UL label.

The PLC compressor control system consists of a programmable logic controller for the monitoring, protection and control of the compressor systems.

Standard features of the CCP include:

- A NEMA  type 4 electrical enclosure

- UL electrical panel

- Human Machine Interface (HMI) with Multi-Color Touch Screen Display incorporating vivid TFT (Thin Film Transistor) Technology and NOT limited by touch cells (Optional mounting configurations available-up to 25 ft remote)

- Emergency Stop Palm Button

- Home screen customizable with distributor contact information

- Real Time Clock  (time and date)

- Compressor on / off

- Digital Display of Compressor Final Pressure

- Digital Display of Compressor Oil Pressure

- Digital Display of current Compressor Run Time

- Digital Display of Final Separator Cycle Count

- Compressor High Temperature Shutdown and Alarm

- Full support of the Automatic Condensate Drain system (interval and duration set points adjustable thru the HMI - password protected)

- Digital Display of time to next ACD Cycle

- Condensate Drain Reservoir full alarm

- Full support of CO monitor alarm functions (optional)

- Full support of SECURUS purification system moisture monitor warning and alarm functions

- Built in overtime timer set at 5 hours - optional times available

- Maintenance Timer (selectable between real time or compressor run time) to give Digital Display of all needed Preventative Maintenance Evolutions

- Motor overload alarm

- Nonresettable hourmeter

- Recoverable Run History (last 5 run periods)

- Recoverable Alarm History (last 5 fault shutdowns)

- Support of up to 5 Languages (to be specified at time of order; includes English, French, Spanish & Portuguese)

- Operator choice of display in BAR or PSI

For ease of Maintenance and Repair:

- PLC has removable Terminal Blocks for all functions

- Diagnostic EEPROM (Electrically Erasable Programmable Read-Only Memory) Capability

- Support of Two (2) Communication Protocols (optional)

  - Ethernet Connection

  - Analog Phone Modem

-    Wiring shall be encapsulated within a split corrugated type loom.   Each wire end

connection shall be machine crimped and numbered.

Affixed to the panel shall be a non-glare Lexan overlay with an integral operating instruction pictogram

The HMI shall have 22 adjustable system parameters secured by password protection.  The HMI will provide display of all safety / fault shutdowns with a text read-out of up to three potential causes for the fault / shutdown.

The compressor oil pressure shall be monitored by a pressure transmitter and digitally displayed on HMI.  The compressor shall shut down and a fault will be indicated on the HMI should the compressor’s oil pressure drop below the factory preset value during operation.  The oil pressure transmitter shall be by-passed during start-up to permit the oil pump to achieve the normal operating pressure.

The low oil pressure and final air pressure transmitters shall be equipped with sealed electrical connectors.  The analog pressure sensors for oil pressure and final pressure shall have adjustable set point and dead-band thru the HMI (password protected).

A temperature switch shall be supplied on the head of the final stage of compression.  The compressor shall shutdown and a fault will be indicated on the HMI should the final stage  temperature exceed the tamper-proof set point during operation.

Purification System

The purification system shall purify high pressure air to a quality that meets or exceeds the requirements of CGA Pamphlet G-7, Compressed Air for Human Respiration, ANSI/CGA G-7.1, Commodity Specification for Air, Grade E, and all other recognized standards for breathing air.  Purification shall be achieved by mechanical separation of condensed oil and water droplets, adsorption of vaporous water by a desiccant, adsorption of oil vapor and elimination of noxious odors by activated carbon and conversion of carbon monoxide to respirable levels of carbon dioxide by catalyst.

The high pressure purification chambers shall have a working pressure of 5000 PSIG.  The purification system shall utilize replaceable cartridges.  The purification system shall be designed so that the replacement of the cartridges can be accomplished without disconnecting system piping.  The design of the chambers shall preclude the possibility of operating the system without cartridges installed or with improperly installed cartridges.  A bleed valve shall be provided to vent the purification system to facilitate replacing the cartridges.  A pressure maintaining valve and a check valve shall be supplied downstream of the purification system to increase the efficiency of the purification system by maintaining a positive back pressure.  A check valve shall be supplied between the coalescing separator on the compressor’s discharge line and the purification system to maintain the positive pressure in the purification system when the compressor shuts down.

The purification system shall include Bauer’s patented Securus Electronic Moisture Monitor System.  A sensor shall be located in the Securus purifier cartridge for direct monitoring of moisture levels.  The Touch Screen Display shall indicate the status of the Securus cartridge.  The Securus system shall warn the operator, in advance, of the impending expiration of the Securus cartridge.  The compressor shall shut down automatically should the operator fail to change the Securus cartridge within the warning period.  The compressor shall not be capable of restarting until the used cartridge is replaced with a new one.  The moisture monitoring system shall be of a fail-safe design.  Should the electrical contact between the display module and sensor be disconnected, an immediate fault shut down shall be effected.  For absolute safety and highest quality breathing air, no manual override shall be supplied for the moisture monitor.

Testing and Preparation for Shipment

The system shall be tested by the manufacturer prior to shipment.  A copy of the manufacturer’s test report shall be available upon request.

A manufacturer’s nameplate shall be securely affixed to the electrical box.  The nameplate shall include, at a minimum, manufacturer’s name, model number and serial number, compressor block number, system operating pressure, compressor operating speed, compressor capacity and charging rate, motor horsepower, voltage, frequency, amperage and date of manufacture.

The system shall be suitably prepared for motor freight transport.  The system shall be bolted to a wooden pallet, wrapped in sheet plastic, and fully protected by 1 x 4 wood framing.  The compressor intake and similar openings shall be suitably covered.  Component parts, loose parts or associated spare parts shall be packaged separately and shipped on the same pallet if feasible.

Documentation

A documentation package shall be supplied with the system.  The documentation package shall include, at a minimum, an operation manual, recommended spare parts list, warranty information and a start-up/warranty registration form.

The Operator’s Instruction and Maintenance Manual for the system shall be as detailed as possible, outlining all operation and maintenance instructions.  The manual shall include detailed illustrated drawings for the compressor block and all system components along with a complete parts listing for all illustrated components.  Warnings and safety precautions shall be identified clearly in the manual.

Available Accessories

The following shall be offered by the manufacturer as accessories to the system:

- Carbon monoxide monitor with calibration kit

- Storage systems

- Fill stations

- DPS-2, Dual Pressure Switch

- Visual CO/Moisture Indicator

Reference outline dimension drawing: ASY-1040

6000 PSIG available;  see MVT19H specification

Please consult the Bauer factory for applications outside of this temperature range.

Based on standard inlet conditions.

Based on recharging an 80 cu ft cylinder from 500 to 3000 PSIG.

Based on an inlet temperature of 70°F.

U. S. Patent Number 4,828,589

Replace all cartridges at the same time.